OUTDOOR ATS 40KVA

GreenPole power solutions India Pvt Ltd

#5/2, Ground Floor, Baretena Agrahara, Hosur Road

Lavakusha Nagar,Electronic City, Bengaluru – 560100,

Phone: +91-80-48666876

Website: www.greenpole-ps.com

PARTCODE: PMGPPS0175

Version: 1.0

Data: 29-APR-2025

Table of Content

1.	Declaration	2

2.	Warning Statements and Safety Symbols	2

3.	General Safety Precautions	3

4.	Electrical Safety	3

5.	Delivery	6

6.	Technical Support Helpline	6

7.	Overall Product Dimension and Grouting Detail	6

8.	Transportation, Unloading and Unpacking	7

8.1.	Dos and Don’ts	8

8.2.	Installation Requirements	8

8.3.	Requirements for Cable Routing	9

8.4.	System Installation	9

9.	System Configuration	11

10.	ATS Controller	11

10.1.	AMF Controller	11

10.2.	Operating modes of AMF Controller	11

10.3.	Protection / Supervision Mains	12

10.4.	Protection / Supervision DG	12

10.5.	Switches Description:	12

10.6.	LED Annunciations description:	13

10.7.	Setting procedure:	13

10.8.	Connection details:	14

10.9.	Technical specification:	14

10.10.	System Single Line Diagram	15

10.11.	Alarms & communication termination details	15

10.12.	Default Configuration	15

11.	Commissioning of Outdoor ATS	21

11.1.	Installation	21

11.2.	Inspection Installation	21

11.3.	Functional Testing	22

12.	Outdoor ATS Maintenance	22

12.1.	Routine Maintenance	22

12.2.	Circuit Breaker Replacement	24

13.	Warranty Exclusion & Recommendation	24

13.1.	Conditions or scenarios where the warranty does not apply, such as:	24

13.2.	Climatic and Environmental Conditions	24

13.3.	Additional Recommendation	25

14.	Outdoor ATS I&C Acceptance Report	26

Foreword

# Declaration

This document provides the GreenPole Outdoor ATS product introduction, safety and proper handling, Installation and commissioning and system instructions. This product should be used under the specified environment condition specified in this document such as input voltage, operating temperature, and humidity, etc.

# Warning Statements and Safety Symbols

| DANGER | Indicates the presence of a hazard that will cause death or severe personal injury if the hazard is not avoided. |
| --- | --- |
| WARNING | Indicates the presence of a hazard that can cause death or severe personal injury if the hazard is not avoided. |
| CAUTION | Indicates the presence of a hazard that will or can cause minor personal injury or property damage if the hazard is not avoided. |
|  | This symbol identifies the need to refer to the equipment instructions for important information |
|  | These symbols (or equivalent) are used to identify the presence of hazardous ac mains voltage. |
|  | This symbol is used to identify the presence of hazardous ac or dc voltages. It may also be used to warn of hazardous energy levels. |
|  | One of these two symbols (or equivalent) may be used to identify the presence of rectifier and battery voltages. The symbol may sometimes be accompanied by some type of statement, for example: “Battery voltage present. Risk of injury due to high current. Avoid contacting conductors with un-insulated metal objects. Follow safety precautions.” |
|  | One of these two symbols may be used to identify the presence of a hot surface. It may also be accompanied by a statement explaining the hazard. A symbol like this with a lightning bolt through the hand also means that the part is or could be at hazardous voltage levels. |
|  | This symbol is used to identify the protective safety earth ground for the equipment. |
|  | This symbol is used to identify other bonding points within the equipment. |
|  | This symbol is used to identify the need for safety glasses and may sometimes be accompanied by some type of statement, for example: “Fuses can cause arcing and sparks. Risk of eye injury. Always wear safety glasses.” |

The symbols may sometimes be accompanied by some type of statement, e.g., “Hazardous voltage/energy inside, Risk of injury. This unit must be accessed only by qualified personnel.”

# General Safety Precautions

- Ensure that the product is used in environments that meet its design specifications to avoid damaging components and voiding the warranty.

- Ensure that only trained and qualified personnel install, operate, and maintain equipment.

- Comply with local laws and regulations. The safety instructions in this document are only supplements to local laws and regulations.

- Do not operate the device or cables during thunderstorms.

- Remove metal objects such as watches, bracelets, and rings when using the product.

- Use insulated tools on the product.

- Follow specified procedures during installation and maintenance.

- Measure contact point voltage with an electric meter before touching a conductor surface or terminal. Ensure that the contact point has no voltage, or it is within the specified range.

- Note that the load may power off during maintenance or fault location if the power system is not

- Connected to a battery or if battery capacity is insufficient.

- Store cables for at least 24 hours at room temperature before laying out them if they were previously stored at sub-0ºC.

- Routinely check installed equipment and perform maintenance according to the user manual; replace faulty components quickly to ensure that the device works properly.

# Electrical Safety

Ground Connection

When installing equipment, protective ground wire must be installed first; when removing the equipment, the protective ground wire must be removed at last. Ensure that equipment is reliably grounded before power on.

High Voltage

|  | High voltage potential is present in some parts inside the power system while operational, direct, or indirect contact with these objects through the wet parts will bring fatal danger. AC power line connection may cause a short-circuit, fire or electric shock accident. AC cable connection and the area wire covered must follow the relevant regulations and design specifications. Peoples, who performed high voltage operations, must have high voltage, AC, and other operations qualifications. |
| --- | --- |

- Obey relevant industry safety standards and design specifications during equipment installation or operation.

- Put up "No Operation" signage on the device or switch can’t be operated during the installation process.

Tools

|  | Use special tools instead of common or homemade tools during high voltage and AC operation. |
| --- | --- |

|  | Never make DC positive pole and DC negative pole short circuit or non-grounded pole (terminal) shorted to ground in power system during operation. The power equipment is constant voltage DC power equipment, a short circuit will cause strong electric arc or fire, endangering the safety of persons and equipment. |
| --- | --- |

Short Circuit

- Never wear watches, bracelets, rings, or other conductive accessories when operating.

- Insulated tools must be used when installing and operating.

- Pay attention to the effect on the hot-line work generated by operating space, furnish the insulating protective measures in the operating area to avoid a short circuit dangerous caused by tool stuck or tool fall off when necessary.

|  | Non-high voltage, AC jobs in thunderstorms. |
| --- | --- |

Thunderstorm

- The atmosphere will produce a strong electromagnetic field in a thunderstorm. To avoid damage to equipment caused by lightning, you should ensure that the equipment has a good grounding.

|  | This product should be placed away from the liquid area, do not install in the vent, air conditioning, machine room outlet window and other prone to water leakage position below, prevent liquid into the equipment caused by short circuit. It is strictly prohibited to put the equipment in flammable, explosive, corrosive gas or smoke environment, and any operation in such environment is strictly prohibited. |
| --- | --- |

Liquid Proof, Explosion Proof

- Do not use water to flush internal and external electrical components of equipment.

- If water, moisture, or condensation is found in the cabinet, please turn off the power immediately. When operating in humid environment, should strictly prevent water and other conductive liquid into the equipment.

|  | Before installing, operating, and maintaining batteries, read the instructions provided by the battery vendor. For more safety precautions, see the instructions provided by the battery vendor. |
| --- | --- |

Mechanical Safety

Hoisting Devices

- Only trained and qualified personnel can perform hoisting operations.

- Before hoisting objects, ensure that hoisting tools are firmly fixed onto a weight-bearing object or wall.

- Ensure that the angle formed by two cables is less than 90 degrees.

Using a Ladder

- Use only ladders that are in good condition. Find out and do not exceed the maximum weight capacity.

- The recommended angle for a ladder against another object is 75 degrees. Measure the gradient with a right angle or your arms, as shown in Figure 1-1. Ensure that the wider end of the frame is at the bottom, the base cannot slide, and that the ladder is securely positioned.

Figure 1-1 correct angle for ladders

###### When climbing a ladder:

- Ensure that your body's center of gravity does not shift outside the legs of the ladder.

- To minimize the risk of falling, steady your balance on the ladder before performing any operation.

- Do not climb higher than the fourth rung from the top.

- To climb onto a roof, ensure that the ladder top is at least one meter higher than the roofline, as shown in Figure 1-2.

###### Moving Heavy Objects

- Be cautious to prevent injury when moving heavy objects.

- Wear protective gloves when moving heavy objects.

Other Considerations:

Acute angle of objects

|  | It is strictly prohibited to modify the structure of equipment and change the position of plate parts without authorization. It is strictly forbidden to change components without authorization and drill holes on the cabinet without authorization. Non-compliant changes will affect the heat dissipation of equipment, electromagnetic shielding and other performance, self-drilling will also lead to metal chips into the cabinet resulting in short circuit board. |
| --- | --- |

Object Angle

|  | Wear protective gloves when handling equipment or removing the equipment packing case with hands to prevent from being cut. |
| --- | --- |

# Delivery

When delivered, inspect the package integrity and the physical conditions of the cabinets carefully.

In case of any damage sustained during transport, immediately inform the carrier, and contact your local Service Center. A detailed report of the damage is necessary for any insurance claim.

|  | NOTE! A DAMAGED CABINET MUST NEVER BE INSTALLED AND COMMISSIONED |
| --- | --- |

# Technical Support Helpline

In case of any support in regard of Installation & Commissioning and operation troubleshooting contact following no. and email.

| Technical support helpline no’s: | Level-1: |
| --- | --- |
|  | Level-2: +91 8095398333 |
|  | e-mail: support@greenpole-ps.com |

# Overall Product Dimension and Grouting Detail

GreenPole Outdoor ATS modularized design and combined structure. It consists of parts such as ATS controller, DG battery charger & ACDB is mainly used to provide power supply for small and medium-sized station equipment.

System dimensions from all sides and grouting (mounting) details shown in Figure 7.1 to 7.3 Figure

Figure 7.1: External Dimensions of Outdoor ATS

7.2 Mounting Dimension Top view

Figure 7.3: Grouting dimensions of Outdoor ATS (Bottom View)

Transportation, Unloading and Unpacking

- The Outdoor ATS cabinet is packed on a suitable pallet to be handled by a forklift or a crane

- Pay attention to the center of gravity

- Move the Outdoor ATS cabinet in its original package until its destination for installation

- Do not stack other packages on top of the cabinet. It could damage it

- The Cabinet should be strapped and buckled during transportation show that it won’t topple or fall from the carrier.

- If the battery cabinet is to be lifted by a crane, use suitable lifting straps and separator bars.

- Take all the necessary precautions to avoid damage to the cabinet for loading and unloading from the carrier.

- Once unloaded position the cabinet on the uniform plinth. Now start unpacking the carton and inspect the cabinet condition if any damaged observed inform the authority to take necessary action. In any case damaged cabinet can be installed at the site.

## Dos and Don’ts

| Dos | Don’ts |
| --- | --- |
| Read and understand this “User Manual” | Do not dismantle the system without authorized service Engineer |
| Always use Insulated tools only for any field activity and Follow PPE during all site related activity. | Do not place metallic objects on the system. |
| Follow Installation and commissioning steps as specified in the manual. Make sure of grounding connection first connected while installation and last removed while decommissioning. | Don’t Leave the ground wire open |
| After I&C completed close & lock the system doors properly & handover the key to customer representative with sign off document duly signed. | Don not Leave equipment exposed to rain or dusty environment by keeping its door open. |
| DO Keep all connected MCB/MCCB always in ON position | Do not keep unused MCB/MCCB in ON position |
| Do close wire gutter covers after installation completed | Do not leave open wire gutter covers & cable grommets |

## Installation Requirements

Construction Personnel Requirements

Only trained and qualified construction personnel are allowed to perform the installation.

Our company will not be liable for the damage to devices or injury to humans caused by failure to follow instructions in this document.

Before installation, pay attention to the following items:

The customer's technical engineers must be trained and be familiar with the proper installation and operational methods. The number of installation personnel varies based on the project progress and the installation environment. Typically, two to four persons are required.

Tools Requirements

Use tools with insulated handles!

Introduction of tools and instrumentation (including, but not limited to, use of the following table tools) required before installation operations are performed.

Table 8.2 Tools and meters

| Tools and Meters |  |  |  |  |
| --- | --- | --- | --- | --- |
| Pallet truck | Ladder | Hammer drill & drill bit | Utility knife | Heat gun |
| Rubber mallet | Insulated adjustable wrench | Multimeter | Flat-head screwdriver | Phillips screwdriver |
| Ruler | Insulated torque wrench M5 to M12 | Cable tie | Wire nippers | Insulation gloves |
| Polyvinyl chloride (PVC) insulation tape | Combination wrench | Heat shrink tubing | Crimping pliers | Insulation protective shoes |
| Hydraulic pliers | Diagonal pliers | Wire stripper | Measuring tape | Marker |

## Requirements for Cable Routing

- Cables should be more than 50mm away from heat sources to prevent insulation layer damage (melting) functional degradation (aging or breakage).

- The bending radius of cables should be at least five times the diameter of the cables.

- Cables of the same type should be bound together. Cables of different types should be a minimum of 30 mm from each other to avoid tangling.

- Cables that are bound together should be close to each other, tidy, and undamaged.

- Ground cables must not be bound to or tangled with signal cables. There should be an appropriate distance between them to minimize interruptions.

- Power cables must be routed straight. No joints or welding should be performed on power cables.

- Use a longer cable if necessary.

## System Installation

- When moving equipment by hand, wear protective gloves to prevent cutting of objects

- It is strictly prohibited to modify the structure of equipment and replace the position of plate parts without authorization, to replace components without authorization, and to drill holes on the cabinet without authorization. Non-conforming changes will affect the heat dissipation of equipment, electromagnetic shielding and other performance, self-drilling will also lead to metal chips into the cabinet, resulting in circuit board short circuit

- According to the specific situation of the site, select the rack placement position, the placement is based on the principle of considering the reasonable inlet and outlet lines of the equipment, leaving no less than 1m space between the front, back, right and left and the wall and other obstacles, and the installation height should be convenient for observation, monitoring and display, while considering the convenience of ventilation, heat dissipation and operation and maintenance, the frame shall be installed horizontally, and the inclination between the cabinet and the horizontal shall not exceed 5°, and shall be fixed on the frame or the floor with bolts, installation procedures of the sub rack are as follows：

Details of inner structure of power system refer below picture：8.4.1 & 8.4.2

Figure 8.4.1: Internal components view

Figure 8.4.2 Internal Components View

# System Configuration

| ITEM | CONFIGURATION |
| --- | --- |
| Grid Input | MCB 1*80A 3P + 1*25 SQMM TB |
| DG Input | MCB 1*80A 3P + 1*25 SQMM TB |
| ATS Output | MCB 1*80A 3P + 1*25 SQMM TB |
| SPD | Class B+C for Grid & Class C for DG |
| Auxiliary control | MCB 1*6A SP + 1*10SQMM TB |
| Alarm TB | 10*2.5 SQMM TB |
| GRID INPUT CABLE RATING | 16SQmm 4core is recommended, the wires of Lines and N are red, Yellow, Blue & black respectively. |
| DG INPUT CABLE RATING | 16SQmm 4core is recommended, the wires of Lines and N are red, Yellow, Blue & black respectively. |
| SYSTEM GROUNDING | 16SQmm Green |

# ATS Controller

ECON is a universal controller for DG Set which can be configured as either automatic or manual controller.

## AMF Controller

- Three Phase Mains Three Phase DG

## Operating modes of AMF Controller

- Manual Mode

- Auto Mode

This mode can be selected by operating through Auto/Manual switch.

- Teat mode

This mode can be selected by pressing the mode switch while unit in auto mode

## Protection / Supervision Mains

- Under/Over Voltage

- Under/Over Frequency

- Phase Sequence

- Voltage Unbalance

## Protection / Supervision DG

- under/Over Voltage

- Under/Over Speed

- Service Due

- Fail To Start (only when configured as AMF controllers)

- Fail To Stop (only when configured as AMF controllers)

- Fault Data Recording: Last 64 fault with date and time stamping

- Event Recording: Last 64 event with date and time stamping

- Password Protection: Three-digit password protection for system settings.

- Real Time Clock (RTC)

- Communication: USB, Fully Isolated RS485

## Switches Description:

ECON has 7 switches provided on its front panel. The table below describes the operation of these.

| Switch Symbol | Switch Function | Description |
| --- | --- | --- |
|  | Next | Normal operation mode: In this mode, it is used to change the parameters being displayed on LCD. Programming Mode: Next key is used to select the next parameter to be programmed. |
|  | Increment /Start | This key has dual function Programming Mode: It is used to increment the value of the parameters under programming. Manual mode: it is used to issue the crank/ start command to DG |
|  | Decrement /Stop | This key has dual function Programming mode: It is used to decrement the value of the parameter under programming. Manual mode: It is used to issue the stop command to DG |
|  | Reset | Reset key resets the Hooter and Fault signals. The first press shall reset the hooter and next shall reset the faults. A long press of 1 Sec shall reset both. |
|  | Programming /History Fault Mode Entry | If both the keys are pressed simultaneously the unit will enter in Programming Mode History Fault/Service Hours |
|  | MCB | In Manual Mode this toggles the mains contactor, On/Off |
|  | GCB | In Manual Mode this toggles the generator contactor, On/Off |
|  | MODE | Toggle between Auto & Test Mode |

## LED Annunciations description:

ECON has nine annunciations on its front panel. These either announce the faults or indicate the status of the system.

| Nomenclature | Symbol | Description |
| --- | --- | --- |
| Auto |  | Led lights up when ECON is in Auto mode |
| Manual Mode |  | Led lights up when ECON is in manual mode |
| Test Mode |  | Led lights up when ECON is in Test Mode |
| Mains Voltage |  | This symbol lights up continuously if Main is healthy else starts blinking. |
| MCB |  | LED turns on in case the mains breaker is switched on or else turned off In manual mode, this LED is switched on by feedback from mains contact on pin 29 |
| GCB |  | LED turns on in case the DG breaker is switched on or else turned off In manual mode, this LED is switched on by feedback from DG contact on pin 28 |
| DG Voltage |  | This indication glows continuously when the generator is running. |
| Warning | Warning | This LED blinks in case of a warning. |
| Fault | Fault | This LED blinks in case of a fault |

Please note: Operating Mode cannot be changed if the unit has stopped in a faulty condition, or the engine is cranking.

Auto, Manual and Test is Radio buttons and only one can be active at a time.

Do not enter manual mode while test mode is operating. Firstly, enter in auto mode then manual mode.

## Setting procedure:

## Connection details:

## Technical specification:

## System Single Line Diagram

## Alarms & communication termination details

## Default Configuration

| Sl.No. | Parameter | Default Value |
| --- | --- | --- |
| System Supply |  |  |
| 1 | Supplier | TMTL |
| 2 | System Configuration | AMF-M:3p/G:3p |
| 3 | Solenoid Type | Pull to Start |
| 4 | J1939 Address | Disable |
| 5 | LLOP Sensor | Disabled |
| 6 | User LLOP R1 | 10 ohm |
| 7 | User LLOP V1 | 0 bar |
| 8 | User LLOP R2 | 29 ohm |
| 9 | User LLOP V2 | 1 bar |
| 10 | User LLOP R3 | 38 ohm |
| 11 | User LLOP V3 | 1.5 bar |
| 12 | User LLOP R4 | 48 ohm |
| 13 | User LLOP V4 | 2 bar |
| 14 | User LLOP R5 | 57 ohm |
| 15 | User LLOP V5 | 2.5 bar |
| 16 | User LLOP R6 | 67 ohm |
| 17 | User LLOP V6 | 3 bar |
| 18 | User LLOP R7 | 86 ohm |
| 19 | User LLOP V7 | 4 bar |
| 20 | User LLOP R8 | 105 ohm |
| 21 | User LLOP V8 | 5 bar |
| 22 | User LLOP R9 | 124 ohm |
| 23 | User LLOP V9 | 6 bar |
| 24 | User LLOP R10 | 143 ohm |
| 25 | User LLOP V10 | 7 bar |
| 26 | Fuel Sensor | Disabled |
| 27 | User Fuel R1 | 10 ohm |
| 28 | User Fuel V1 | 0 |
| 29 | User Fuel R2 | 29 ohm |
| 30 | User Fuel V2 | 0.1 |
| 31 | User Fuel R3 | 48 ohm |
| 32 | User Fuel V3 | 0.2 |
| 33 | User Fuel R4 | 67 ohm |
| 34 | User Fuel V4 | 0.3 |
| 35 | User Fuel R5 | 86 ohm |
| 36 | User Fuel V5 | 0.4 |
| 37 | User Fuel R6 | 105 ohm |
| 38 | User Fuel V6 | 0.5 |
| 39 | User Fuel R7 | 124 ohm |
| 40 | User Fuel V7 | 0.6 |
| 41 | User Fuel R8 | 143 ohm |
| 42 | User Fuel V8 | 0.7 |
| 43 | User Fuel R9 | 181 ohm |
| 44 | User Fuel V9 | 0.9 |
| 45 | User Fuel R10 | 200 ohm |
| 46 | User Fuel V10 | 1 |
| 47 | Fuel Tank Cap | Disable |
| 48 | HET Sensor | Disabled |
| 49 | User HET R1 | 540 ohm |
| 50 | User HET V1 | 40 Celsius |
| 51 | User HET R2 | 458 ohm |
| 52 | User HET V2 | 45 Celsius |
| 53 | User HET R3 | 222 ohm |
| 54 | User HET V3 | 65 Celsius |
| 55 | User HET R4 | 120 ohm |
| 56 | User HET V4 | 85 Celsius |
| 57 | User HET R5 | 93 ohm |
| 58 | User HET V5 | 90 Celsius |
| 59 | User HET R6 | 80 ohm |
| 60 | User HET V6 | 95 Celsius |
| 61 | User HET R7 | 70 ohm |
| 62 | User HET V7 | 100 Celsius |
| 63 | User HET R8 | 60 ohm |
| 64 | User HET V8 | 105 Celsius |
| 65 | User HET R9 | 53 ohm |
| 66 | User HET V9 | 110 Celsius |
| 67 | User HET R10 | 46 ohm |
| 68 | User HET V10 | 115 Celsius |
| 69 | Sensor Open | Disable |
| 70 | CT Ratio | 20 Ratio |
| 71 | Generator RPM | 1500 |
| 72 | Contact Pin 32 | None |
| 73 | Contact Pin 31 | None |
| 74 | Contact Pin 30 | None |
| 75 | Over Load KW | 32.0 KW |
| 76 | Over Current | 60.0 Amps |
| 77 | Over Load Delay | 10 Sec |
| 78 | High Load KW | Disable |
| 79 | High Load Delay | 3600 Sec |
| 80 | D Input 1 | RWL |
| 81 | D Input Plarity 1 | Normal Open |
| 82 | D Input 2 | MAINS MCCB |
| 83 | D Input Plarity 2 | Normal Open |
| 84 | D Input 3 | FUEL |
| 85 | D Input Plarity 3 | Normal Open |
| 86 | D Input 4 | HET |
| 87 | D Input Plarity 4 | Normal Open |
| 88 | D Input 5 | C Door Open |
| 89 | D Input Plarity 5 | Normal Open |
| 90 | D Input 6 | Mains Charger |
| 91 | D Input Plarity 6 | Normal Open |
| 92 | D Input 7 | DG MCCB |
| 93 | D Input Plarity 7 | Normal Open |
| 94 | D Input 8 | Canopy Temp |
| 95 | D Input Plarity 8 | Normal Open |
| 96 | D Input 9 | Remote Start |
| 97 | D Input Plarity 9 | Normal Open |
| 98 | MCB Plarity | Normal Open |
| 99 | Fan High Current | Disable |
| 100 | Mode Change Hr | Disable |
| 101 | Mode Change Warn | 120 Sec |
| 102 | Mode Change | Selector Switch |
| Generator Supply |  |  |
| 103 | Generator Over Volt | 255 V |
| 104 | Generator Under Volt | 185 V |
| 105 | Generator Volt Delay | 15 Sec |
| 106 | Generator Over Freq. | 55.0 Hz |
| 107 | Generator Under Freq. | 45.0 Hz |
| 108 | Generator Freq. Delay | 5 Sec |
| 109 | Current Unbalance IN | Disable |
| 110 | Pick Up Voltage | 30 V |
| 111 | Pick Up RPM | 300 RPM |
| 112 | Service Due Hour | 999 Hrs |
| 113 | Crank Cut Method | Volt ,Freq |
| AMF / Main Supply |  |  |
| 114 | Main Over Voltage Trip | 280 V |
| 115 | Main Over Voltage Return | 275 V |
| 116 | Main Under Voltage Trip | 145 V |
| 117 | Main Under Voltage Return | 165 V |
| 118 | Mains Volt Delay | 10 Sec |
| 119 | Mains Over Frequency | 55.0 Hz |
| 120 | Mains Under Frequency | 45.0 Hz |
| 121 | Mains Frequency Delay | 5 Sec |
| 122 | Mains Restor Time | 30 Sec |
| 123 | WarmUp Time | 10 Sec |
| 124 | Gen Start Delay | 0 Mins |
| 125 | Gen On Time | 210 Mins |
| 126 | Gen Rest Time | 10 Mins |
| 127 | Mains Over Load | Disable |
| 128 | Contactor Protection | Enabled |
| 129 | Mains Fail | All Phases Fail |
| 130 | GCB To MCB Delay | 5 Sec |
| 131 | Recooling Time | 60 Sec |
| 132 | Service Delay Hrs | Disable |
| 133 | Service Run Min | 1 Mins |
| Protection List |  |  |
| 134 | Fuel Warn Level | 0.5 |
| 135 | Fuel Warn Delay | 10 Sec |
| 136 | Fuel Trip Level | 0.15 |
| 137 | Fuel Trip Delay | 10 Sec |
| 138 | LLOP Trip Level | 0.7 Kg/cm2 |
| 139 | LLOP Trip Delay | 10 Sec |
| 140 | HET Trip Level | Disable |
| 141 | D. Input 1 Delay | 10 Sec |
| 142 | D. Input 2 Delay | 10 Sec |
| 143 | D. Input 3 Delay | 10 Sec |
| 144 | D. Input 4 Delay | 10 Sec |
| 145 | D. Input 5 Delay | 10 Sec |
| 146 | D. Input 6 Delay | 180 Sec |
| 147 | D. Input 7 Delay | 10 Sec |
| 148 | D. Input 8 Delay | 10 Sec |
| 149 | D. Input 9 Delay | 1 Sec |
| 150 | CHG Alternator | Disable |
| 151 | Hooter On Time | 30 Sec |
| 152 | Crank OnTime | 5.0 Sec |
| 153 | Crank Gap Time | 10 Sec |
| 154 | Crank Attempts | 3 |
| 155 | Solenoid On Time | 30 Sec |
| 156 | Auto Scroll On/Off | OFF |
| 157 | Battery/Supercapacitor UV Warn | 10.0 V |
| 158 | Battery/Supercapacitor OV Warn | 14.5 V |
| 159 | Remote on | Disable |
| 160 | NESA Dis/Enab | Disable |
| 161 | NESA OFF Time | 23:59 Hr:Min |
| 162 | NESA ON Time | 23:59 Hr:Min |
| 163 | NCD Strategy | Disable |
| 164 | NCD Warn Hrs | 36 |
| 165 | NCD Fault Hrs | 72 |
| 166 | NCD Heal Hrs | 40 |
| BTS |  |  |
| 167 | BTS Under Voltage | 47.5 V |
| 168 | BTS Voltage Delay | 20 Sec |
| Annuciation |  |  |
| 169 | Ann Mains OK | No Annunciation |
| 170 | Ann Mains NOK | No Annunciation |
| 171 | Ann DG ON | No Annunciation |
| 172 | Ann DG OFF | No Annunciation |
| 173 | Ann Fuel Trip | No Annunciation |
| 174 | Ann LLOP Trip | No Annunciation |
| 175 | Ann HET Trip | No Annunciation |
| 176 | Ann DG VOL | No Annunciation |
| 177 | Ann Emergency | No Annunciation |
| 178 | Ann DG O/L | No Annunciation |
| 179 | Ann DG Freq | No Annunciation |
| 180 | Ann RWL Fault | No Annunciation |
| 181 | Ann Chg/VBelt | No Annunciation |
| 182 | Ann Fail Start | No Annunciation |
| 183 | Ann Fail Stop | No Annunciation |
| 184 | Ann Current Unbalance | No Annunciation |
| 185 | Ann Fuel Open | No Annunciation |
| 186 | Ann LLOP Open | No Annunciation |
| 187 | Ann HET Open | No Annunciation |
| 188 | Ann Cannopy | No Annunciation |
| 189 | Ann Fire | No Annunciation |
| 190 | Ann Oil Temp | No Annunciation |
| 191 | Ann Oil Level | No Annunciation |
| 192 | Ann Mains O/L | No Annunciation |
| 193 | Ann Service Due | No Annunciation |
| 194 | Ann Batt/Supercapacitor NOK | No Annunciation |
| 195 | Ann BTS 1 NOK | No Annunciation |
| 196 | Ann Reserved | No Annunciation |
| 197 | Any Common Fault | No Annunciation |
| 198 | Half Fuel | No Annunciation |
| 199 | C Door Open | No Annunciation |
| 200 | Ann DG in Manual | No Annunciation |
| 201 | Ann DG Not in Manual | No Annunciation |
| 202 | Ann Unit Ok | No Annunciation |
| 203 | Ann Mode Change Warn | No Annunciation |
| 204 | Ann CPCB4+ Audio | No Annunciation |
| 205 | Ann J1939 1 | No Annunciation |
| 206 | Ann J1939 2 | No Annunciation |
| 207 | Ann J1939 3 | No Annunciation |
| 208 | Ann J1939 4 | No Annunciation |
| 209 | Ann EGR Warn | No Annunciation |
| 210 | Ann NCD Warn | No Annunciation |
| 211 | Ann NCD Fault | No Annunciation |
| Device Communication Setting |  |  |
| 212 | Device ID | 34 |
| 213 | Baud Rate | 9600 |
| 214 | Device Parity | NONE |
| 215 | Stop Bits | One |

# Commissioning of Outdoor ATS

## Installation

Check that all input and output circuit breakers or fuses are in off state. All input and output connection cables, signal wires, working ground wires and protective ground wires are firmly connected.

Check box and earthing grounding resistance is not higher than 0.1 Ω between components.

Refer the SLD and perform connection as per below sequence.

Install Earth/ Ground cable

Step 1: Insert the Earth/Ground cable through the hole on the right side of the Cable entrance through the cable gland and tight it.

Install AC input cable (Grid and DG)

- Make sure the front AC input is left open to an OFF state and place a prominent "do not operate" sign.

- Put all MCB OFF before installing the cable.

Step 1: Connect the 220AC Ph-Neu 2-wire Grid AC input cable through the cable entry bottom

Step 2: Fastening the AC input line to the corresponding AC input terminal.

Step 3: Connect the 220AC Ph-Neu 2-wire DG AC input cable through the cable entry bottom

Step 4: Fastening the DG input line to the corresponding AC input terminal.

## Inspection Installation

- Check hardware installation

  - Check that all screws are properly fastened (especially those used for electrical connections) and that the flat washer and spring washer are properly installed.

  - Check that the rectifier module is fully inserted into each slot and locked correctly.

- Check electrical connection

  - Check that all MCB are OFF.

  - Check that the flat washer and spring washer are securely installed on all the terminals, and that all OT terminals are complete and correctly connected.

  - Check whether the battery is properly installed and whether the battery cable is properly connected.

  - Check that the input and output power cables and ground cables are properly connected.

- Check the cable installation

  - Check the cable installation

  - Check that all cables are lined up neatly and tightly connected to their nearest cables, without twisting or overly bending.

  - Check cable label is correct, firm, and consistent.

## Functional Testing

Auto mode:

- Check all cables are connected properly, tighten properly & no short in between Line & Neutral or Line to Earth.

- Check the Input supply voltage is within the range and polarity (Line & neutral)

- Connect auxiliary power supply 48VDC from HPS

- Switch on Aux MCB and verify ATS controller power on

- Keep all output MCB’s in OFF position & switch ON the Grid Input MCB and verify the contactor function and then check voltage at all output MCB/MCCB.

- After confirming Grid operation, switch OFF the Grid input MCB and verify system ON battery mode. If BTS voltage is <47.5V check DG crank and then switch ON DG input MCB and verify the contactor function and check the output voltage.

- Switch on the output MCB/MCCB and check the voltage at end termination is healthy.

Manual mode:

- The engine must be started manually by manually pressing “Start” switch or start at DG end manually.

- Switch ON the DG input MCB and Press the GCB button in ATS controller & verify the DG contactor is ON and ensure output voltage

- To stop the generator, switch OFF the GCB contactor by pressing GCB and press “STOP” switch

- Switch ON the Grid input in Manual mode. Press the MCB button in ATS controller and verify the Grid (C1 & C3) contactor is ON and ensure output voltage.

# Outdoor ATS Maintenance

## Routine Maintenance

Routine maintenance is to find out the potential causes of failure in time before the failure of the equipment affects the business and to carry out effective maintenance. Processing to avoid business impact. Maintenance engineers must be familiar with relevant site conditions before maintenance and be prepared with maintenance tools in advance. The system can work continuously and uninterruptedly. In order to ensure the reliability of power supply, it is necessary to do a good job in daily maintenance to make the power supply system work in the best state.

- Regular cleaning of the system (Air filters, door gasket and cable entry & exit) to prevent dust accumulation and other phenomena every week or 15 days once. (Based on the site environmental condition)

- Check the parameters of the power system once a week if they are normal. If there are abnormalities, they should be eliminated in time.

- Every month or after the thunderstorm should check whether the lightning protector is invalid, if it is invalid, it should be replaced in time.

- Check the MCB/MCCB status once a month, check the connection of input and output wiring loosening and bad contact once a month.

- Check every month whether the input and output conductors are intact and intact. If there is any damage, they should be replaced in time. Check every circuit breaker once a half year whether it can switch flexibly, whether it burns or not.

- Maintenance and maintenance of batteries shall be carried out in accordance with the relevant instructions of batteries.

Table 12.1.1 List of Periodic Maintenance

| Maintenance items | Maintenance content |  |  |
| --- | --- | --- | --- |
|  | Checkpoints | Inspection methods | processing method |
| Appearance of cabinet | No damage to locks of cabinet doors | Visual inspection, switch door lock | Lock changing |
|  | Cabinet damaged and deformed | Visual inspection | If the damage is serious, the cabinet should be replaced. |
|  | Is there corrosion and rust in cabinet | Visual inspection | Re-painting after rust removal |
|  | Does the cabinet have dust, oil and other covering | Visual inspection | Clean with soft cotton cloth |
| Dustproof net | Are there any ash deposits | Visual inspection | Clean up |
| Temperature in cabinet | Is it too high or too low | Thermometer measurement | Take reasonable heating or cooling measures. |
| system output | Is Voltage Output Normal | A multimeter | Refer to Fault Analysis and Handling |
| indicator | if the indicator is normal | Visual measurement | Refer to Fault Analysis and Handling |
| Wireway | Whether the insulating layer and terminal are damaged or not | Visual measurement | Replacement of cables or insulated terminals |

## Circuit Breaker Replacement

Preparation in advance

- Prepare tools and materials: anti-static wristband/anti-static gloves, cross screwdriver, one-word screwdriver, anti-static box/anti-static bag, cabinet door key.

the front power source must be disconnected before the circuit breaker is replaced.

Operational steps

- Wear anti-static wristband or gloves. And disconnect the power source of the front stage.

- Remove the cables/busbars on the circuit breaker in turn with cross/star type screwdrivers. Insulate the cables in time and label them in the process of disassembly.

- Use a screwdriver unscrew mounting hardware’s, and then remove the circuit breaker.

- After replacing circuit braker connect back wires/busbars back to original position

# Warranty Exclusion & Recommendation

## Conditions or scenarios where the warranty does not apply, such as:

- Improper handling, transportation, installation, use or maintenance.

- Damage due to accidents, natural disasters or environmental conditions (Flod, Earth quack, Fire, High wind etc.) outside the specific/product range.

- Unauthorized repairs or modifications, addition of external equipment and tempering cases.

- Abnormal input to the system and related product.

- Costs that may be incurred by the customer, such as shipping or handling fees or special request to support.

## Climatic and Environmental Conditions

Dust and Particulate Matter:

- Adopt proper and routing maintenance for dust and particulate levels in the operating environment.

- Necessity of filters, enclosures, Rack & Rectifier cleaning to protect the Power system and related product

Recommendations:

- Regular Maintenance-Weekly basis to ensure optimal performance and longevity.

Corrosive Environments:

- Restrictions on operating the Power System in corrosive environments.

- Recommend protective measures or coatings if necessary.

Recommendations:

- Regular Maintenance-Weekly basis to ensure optimal performance and longevity.

Electrical Environment:

- Requirements for input voltage, frequency, and power quality must be as specified on product and manual.

- Surge protection and grounding maintained as recommended.

Operating Temperature Range:

- Minimum and maximum operating temperatures must be as specified (e.g., 0°C to 50°C).

- Temperature-related conditions that could affect warranty coverage.

Altitude:

- Maximum operating altitude must be withing range (e.g., up to 2000 meters above sea level).

## Additional Recommendation

Record Keeping:

Keeping detailed records of installation, maintenance, and any issues encountered to support potential warranty claims.

# Outdoor ATS I&C Acceptance Report

| ATS CHECK LIST |  |  |  |  |
| --- | --- | --- | --- | --- |
| CUSTOMER: |  | Site In charge Name & Nun: |  |  |
| SITE NAME/CODE: |  | Installation Date: |  |  |
| Commissioning Date: |  | System Sr No: |  |  |
| I&C Eng. Name: |  | Contact No: |  |  |
| VISUAL INSPECTION/OBSERVATIONS |  |  |  |  |
| SL.NO | PARAMETER | OBSERVATION STATUS |  | REMARKS |
| 1 | MOUNTING OF RACK/SUB RACK MECHANICAL NUTS / BOLTS | Ok | Not Ok |  |
| 2 | TIGHTNESS OF ELECTRICAL TERMINATION | Ok | Not Ok |  |
| 3 | LUGGING & CRIMPING OF INSTALLATION CABLES | Ok | Not Ok |  |
| 4 | FIXING OF NUTS & BOLTS AT MOUNTING HOLES | Ok | Not Ok |  |
| 5 | POWER & CONTROL CABLE ROUTING | Ok | Not Ok |  |
| 6 | TERMINATION OF LOAD MCB/MCCB | Ok | Not Ok |  |
| 7 | FIXING OF CABLE GLANDS/GROMMET | Ok | Not Ok |  |
| 8 | DOOR LOCK OPERATION | Ok | Not Ok |  |
| FUNCTIONAL VERIFICATION |  |  |  |  |
| 1 | ATS MANAUL / AUTO MODE | Ok | Not Ok |  |
| 2 | DG START & STOP IN MANUAL MODE | Ok | Not Ok |  |
| 3 | GRID & DG CONTACTOR OPERATION IN MANUAL MODE | Ok | Not Ok |  |
| 4 | GRID & DG CONTACTOR OPERATION IN AUTO MODE | Ok | Not Ok |  |
| 5 | DG REMOTE START SIGNAL IN AUTO MODE | Ok | Not Ok |  |
| 6 | GRID & DG CONTACTOR FEEDBACK | Ok | Not Ok |  |
| 7 | DG BATTERY CHARGER OPERATION | Ok | Not Ok |  |
| 8 | AC-DC CARD OPERATION | Ok | Not Ok |  |
| 9 | GRID INPUT & DG INPUT VOLTAGE SENSING | Ok | Not Ok |  |
| 10 | ATS OUTPUT VOLTAGE at ALL OUTPUT POINTS | Ok | Not Ok |  |
| 11 | SPD FAIL ALARM | Ok | Not Ok |  |
| 12 | BTS & DG BATTERY VOLTAGE SENSING | Ok | Not Ok |  |
| 13 | DG START FOR BTS BATTERY VOLTAGE LOW | Ok | Not Ok |  |
| 14 | ATS CONTROLLER RS485 COMMUNICATION | Ok | Not Ok |  |
| GREENPOLE POWER SOLUTIONS |  | CUSTOMER |  |  |
| NAME: |  | NAME: |  |  |
| DESIGNATION: |  | DESIGNATION: |  |  |
| CONTACT NO: |  | CONTACT NO: |  |  |
| DATE: |  | DATE: |  |  |
| SIGNATURE: |  | SIGNATURE: |  |  |